## РСК миниЦОД - Техническая спецификация

|  |
| --- |
| **ОБЩАЯ ИНФОРМАЦИЯ** |
| **Архитектура** | [Кластерная архитектура РСК Торнадо](http://www.rscgroup.ru/ru/our-technologies/266-klasternaya-arhitektura-rsk-tornado) |
| **Особенности** | Законченное решение всего в 2-х шкафах, включающая:* Жидкостное охлаждение электронных компонентов;
* Коммуникационная подсистема;
* Подсистема хранения;
* Единая точка мониторинга и управления всей системой
 |
| **Отличительные особенности** | * Низкий уровень шума;
* Энергоэффективность;
* Отсутствие подвижных компонентов (таких, как вентиляторы, жесткие диски, используются твердотельные накопители SSD);
* Компактный размер;
* Отсутствие необходимости в оборудовании помещения системами кондиционирования воздуха;
* Высокая скорость развертывания системы;
* Система может быть установлена в необорудованное помещение
 |

|  |
| --- |
| **ВЫЧИСЛИТЕЛЬНЫЙ ШКАФ** |
| **Тип вычислительного поля** | Гомогенный, с возможностью расширения до Гетерогенного |
| **Производительность (пиковая)** | 0,7 ПФЛОПС |
| **Вычислительные ресурсы** | До 153 базовых расширяемых вычислительных узлов архитектуры x86  (семейств: Intel® Xeon™ E5-2600 v4/v3 или Intel® Xeon® Gold 6100 / Intel® Xeon® Platinum 8100) или архитектуры VLIW (МЦСТ Эльбрус 4С/8С) |
| **Память** | 39.2 ТБ |
| **Управление системой** | Полный интегрированный стек программного обеспечения «РСК БазИС», оптимизированного для высокопроизводительных  вычислений:Единая точка мониторинга и управления всей системой, Гибкая система конфигурирования, система мониторинга и управления всем ЦОД  |
| **Операционные системы** | Linux (RedHat, SUSE, Debian, CentOS, Scientific Linux), MS Windows  / ОС МСВС или ОС Эльбрус |
| **Управление задачами** | SLURM, Altair PSB Professional, Adaptive Computing Moab, IBM Platform LSF |
| **Параллельные файловые системы** | Lustre, Panasas, GPFS, FhGFS и другие |
| **Библиотеки, компилляторы, утилиты** | Intel® Cluster Studio, PGI compilers, стандартные библиотеки MPI |
| **Энергопотребление** | до 70 кВт |
| **Система охлаждения** | Прямое жидкостное охлаждение «РСК Торнадо»: до 100 кВт на вычислительный шкаф;Интеграция с существующей системой охлаждения заказчика (опционально) |
| **Форм-фактор** | 42U |
| **Размеры** | В 2,0 м х Ш 0,8 м х Г 0,8 м |
| **Вес** | До 860 кг |
| **Электропитание** | До 100 А при 400/230 В (три фазы, ноль и заземление) |

|  |
| --- |
| **ИНФРАСТРУКТУРНЫЙ ШКАФ** |
| **Назначение** | Размещение и водо-воздушное охлаждение инфраструктурных подсистем: коммуникационной, хранения данных, мониторинга и управления; ИБП; автономной системы пожаротушения (опция) |
| **Охлаждение** | До 20 кВт тепловой мощности |
| **Форм-фактор** | 42U |
| **Размеры** | В 2,0 м х Ш 0,8 м х Г 0,8 м |
| **Вес** | В зависимости от конфигурации |
| **Электропитание** | В зависимости от конфигурации |



## Пакеты расширения RSC Tornado Expansion Pack



* Пакет расширения **RSC Tornado HPC Expansion Pack**, ориентированный на высокопроизводительные вычисления с использованием двух сопроцессоров Intel® Xeon Phi™ 7120X, позволяет повысить производительность вычислительного узла до 3,74 ТФЛОПС;
* Пакет расширения **RSC Tornado VDI Expansion Pack** предназначен для задач виртуализации и удаленного доступа к рабочим местам, а также областей CAD/CAM/CAE. Построен на основе карт AMD FirePro™ S10000 или NVIDIA GRID™ K1/K2 и высокопроизводительного твердотельного накопителя Intel® SSD DC P3700;
* Программно-аппаратный пакет расширения **RSC SDM Expansion Pack** позволяет реализовать концепцию RSC Software Defined Management, улучшая управляемость и увеличивая доступность вычислительных систем для пользовательских приложений;

Возможно создание и других специализированных пакетов расширения согласно конкретным запросам заказчиков.

## RSC DCmini – Technical Data Sheet

|  |
| --- |
| **TECHNICAL SPECIFICATION** |
| **Architecture** | [RSC Tornado Cluster Architecture](http://www.rscgroup.ru/en/our-technologies/267-rsc-tornado-cluster-architecture) |
| **Features** | * Just 2 cabinets;
* Direct liquid cooling system (“Hot water” mode support);
* Communication system;
* Data Storage;
* Single Point of Monitoring and Management
 |
| **Unique features** | * Low-noise;
* Energy effectiveness;
* Absence of moving parts, such as fans and traditional hard disk drives (solid state drives are used instead);
* Compact;
* Flexible installation options: limited by space and mass requirements only – doesn’t require additional forced air cooling
 |
| **Scalability** | Supported, by DCmini solutions, up to 2 compute cabinets |
| **Cooling** | * Two circuits system:
* Internal – infrastructure cabinet mounted;
* External – can be mounted on the roof, walls and ground or customer’s cooling system integrated.
* Customer cooling system direct integration supported
 |

|  |
| --- |
| **COMPUTE CABINET (BASIC CONFIGURATION)** |
| **Compute Field Type** | Homogeneous (Heterogenous with RSC HPC Expansion Pack) |
| **Performance (RMax)** | 237 TFLOPS |
| **Compute resources** | Up to 128 basic x86 architecture compute nodes  (306 processors, 6732 cores, 13464 threads Intel® Xeon® E5-2699 v4) |
| **Memory** | 39.2 TB |
| **System management** | Fully integrated software stack for High Performance Computing “RSC BasIS”:* Single System Management Point,
* Flexible Software Configuration System,
* Supercomputer and Data Center view and management system
 |
| **Operating Systems** | Linux (RedHat, SUSE, Debian, CentOS, Scientific Linux), MS Windows |
| **Job management** | SLURM, Altair PSB Professional, Adaptive Computing Moab, IBM Platform LSF |
| **Parallel File Systems** | Lustre, Panasas, GPFS, FhGFS and others |
| **Libraries, Compilers and Tools** | Intel® Cluster Studio, PGI compilers, standard MPI libraries |
| **Power consumption** | Up to 70 kW |
| **Cooling** | “RSC Tornado” direct liquid cooling system: up to 100kW per Cabinet;Option: integration with existing customer’s cooling system |
| **Formfactor** | 42U |
| **Dimensions** | H 2.0m (80 in.) х W 0.8m (32 in.) х D 0.8m (32 in.) |
| **Weight** | Up to 860kg (1,874 lbs.) |
| **Power** | Up to 250A at 400/230V (three-phase, neutral and ground) |

|  |
| --- |
| **INFRASTRUCTURE CABINET** |
| **Destination** | Air cooled equipment distribution: Communication equipment, Data Storages, Monitoring andManagement Systems; UPS; Autonomous fire extinguishing system |
| **Cooling** | Up to 20kW heating power |
| **Formfactor** | 42U |
| **Dimensions** | H 2.0m (80 in.) х W 0.8m (32 in.) х D 0.8m (32 in.) |
| **Weight** | Depending on configuration |
| **Power** | Depending on configuration |

|  |
| --- |
| **COMPUTE NODE (BASIC CONFIGURATION)** |
| **Processor** | 16-core Intel® Xeon® E5-2697A v4 (2.6GHz, 32 threads, TDP 145W) or other Intel® Xeon® E5-2600 v4 family processors;2 processors per node;Intel® Turbo Boost Technology is permanently enabled (+300MHz with all cores utilized) |
| **System board** | Intel® Server Board |
| **Memory** | DDR4-2133/2400, up to 256GB per node |
| **Local storage** | Solid State Drives; up to 2 SSDs per node |
| **CommunicationI/O interfaces** | Integrated I/O: FDR InfiniBand, 56Gbps; QDR InfiniBand, 40Gbps; 10 GigE;Optional enhancement (PCIe x16 gen3): Dual-Port InfiniBand EDR, Intel Omni-Path Fabric, Quad-Port 10/40 GigE, FibreChannel |
| **Service I/O interfaces** | 2x GigabitEthernet, IPMIv2 support |
| **Cooling** | Water cooled, coldplate, “Hot Water” mode support |
| **Power** | Independent per node, 180-240V 50Hz |
| **Formfactor** | High Density Blade |
| **Expansion** | Supported, with RSC Expansion Pack |
| **Hot Swap** | Supported, with no influence to any other nodes |

##

## RSC Tornado Expansion Packs



* **RSC Tornado HPC Expansion Pack** focused on high-performance computing with two Intel® Xeon Phi™ coprocessors improves computing node performance to 3,74TFLOPS;
* **RSC Tornado VDI Expansion Pack** is intended for virtualization and remote workplace access and for CAD/CAM/CAE fields. It is based on AMD FirePro™ S10000 or NVIDIA GRID™ K1/K2 cards and on Intel® SSD DC P3700 high-performance solid-state drives;
* Hardware and software package **RSC SDM Expansion Pack** implements Software Defined Management concept developed by RSC specialists for RSC Tornado and RSC PetaStream nodes improving manageability and accessibility of computing systems for user applications. Flexible combination of management agents (infrastructure components, computing nodes, scheduler and user application libraries) within the scope of this concept enables creation of new Task-Oriented Management Applications (TOMA) that improve computing system efficiency and reduce operating costs. One of the examples of this is an application for adaptive management of task scheduler priorities that considers available power resources and actual capacity of data center cooling systems to prevent task termination and resulting loss of critical data on temporary infrastructure failures.

Other specialized expansion packs can also be created on specific requests of the customers. This approach has significantly improved availability of specialized configurations and made modernization process much more easier while preserving record compactness, computing density and power density of solutions based on RSC Tornado cluster architecture.